## CO2
Total Flooding System
CO2 quantity = Hazard remote volume (V) x Flooding Factor
Where:
Flooding Factor for room volume less than 56.6m3 the flooding factor should be 1.6kg CO2/m3
, and for room volume greater than 56.6m3 the flooding factor should be 1.33kg CO2/m3
(NFPA 12, Table 2-4.2.1 )
Input Data
V= | 200 | m3
V= | 7062.9333 | ft3
Flooding Factor= | 1.33
Output Data
CO2 Quantity | 266 | kg
The Required Number of Cylinders |  |  | 6 | Based on the recommended cylinder size is 45 kg

## FM200
Total Flooding System
W = V/S*{C/(100-C)}
Where:
W = weight of clean agent [Ib (kg)].
V = net volume of hazard [ft3 (m3).
S = specific volume of the superheated agent vapor at 1 atmosphere and the temperature, t [ft3/Ib (m3/kg)].
(NFPA 2001, edition 2000, item 3-5.1)
S = 2.2075 (ft3/Ib) at t = 70 (Fo)
(NFPA 2001, edition 2000, Appendix A, table A-3-5.1(k))
Input Data
V= | 200 | m3
V= | 7062.9333 | ft3
S= | 2.2075 |  | If the room temp. will be not be less than 20oC
Output Data
W= | 288.9886 | Ib
| 131.083 | kg
The Required Cylinders Capacity (Ib.)
SUM
Clylider Sizes |  | 17 |  |  |  | 17
Required No. of discharge nozzle
Agent flow rate = W/t
Where t = maximum discharge time (10 sec.)
Agent flow rate = |  | 1.7 | lb/sec
Required No. of discharge nozzle = Total flow rate / average flow rate per nozzle (20 Ib / Sec.)
Required No. of discharge nozzle = |  |  |  | 1 | 0.085
Check the Room Concentration
Check for t = 90 (oF)
C= | 0.5504
The Room Concentration is |  |  | Not Accept